## Slide 1: SOPEEC Sub-Committee November 2014
Proposed National Standard for Plant rating, Plant Classification and Supervision Requirements for Boiler Plants

## Slide 2: SOPEEC Uniform Plant Rating, Plant Classification for Canada
Currently Canada does not have a national standard for the classification, rating and supervision of boilers, steam prime movers, compressors and refrigeration technologies.
Each national region primarily applies variable plant ratings as the basic risk consideration for levels of supervision.

## Slide 3
In 2009 National Public Safety Advisory Committee of Canada (NPSAC) requested that a national standard be developed.
The intent is to provide a uniform Canadian standard for the safe management and operation of boilers.

## Slide 4
It is equally desired that a similar rationale be applied to the technologies of Steam Prime Movers, Compression and Refrigeration in order to provide a national standard, as may be regionally required, for safe and uniform regulation of all Canadian power plants

## Slide 5: Power Engineering Scope of Knowledge
4th Class – Entry level. Restrictions on being the shift engineer and a chief engineer.
20% body of knowledge
3Rd Class – Restrictions on being the shift engineer and a chief engineer.
40 % body of knowledge
2nd Class – No restrictions on being the shift engineer. Restrictions on being the chief engineer.
80% body of knowledge
1st Class – No restrictions.
100 % body of knowledge
The arrow represents the body of knowledge obtained

## Slide 6: Proposed Model for Boiler Plant Rating
Traditionally boilers in plants have been classified as either being high pressure or low pressure boilers.
  In most cases boilers operating above 101 kPa (15 psi ) steam and 1103 kPa (160 psi ) hot water were classified as being high pressure and or power boilers.
  Boilers operating at or below 101 kPa (15 psi ) steam and 1103 kPa (160 psi ) hot water were classified as low pressure and or heating boilers.

## Slide 7
It is recommended by the sub-committee relative to boiler management and operation differences between Low and High Pressure Steam and High Temperature Hot Water that it cannot warrant the regulation of pressure and temperature segregation.

## Slide 8: Benefits of Proposed Change
The benefits of eliminating pressure and temperature segregation includes:
  the current classification and supervisory requirements are primarily based on the risk factor of boiler energy rating rather than pressure/temperature
  simplified regulations
  reduced regulation impact on industry
  a Standard Power Engineers Operating Allowance
  increased practical opportunities for 4th and 3rd class engineers in relation to their academic knowledge

## Slide 9
The proposed model is designed to encourage a central boiler room and a reduced number of boilers.
  This will provide a reduction of equipment failures, reduced maintenance, plant operating errors, and increased safety.

## Slide 10: Proposed Model for Supervision Requirements:
The traditional method of classifying boilers by pressure and temperature has been changed to steam or hot water.
Boilers are now classified as either Steam or Hot Water.

## Slide 11: Five Risk Factors
The proposed model would address five
risk factors.
Total Installed kW Capacity (Steam & Water)
Single or Multiple Boilers
Number of Boiler Rooms
Boiler Type
Fuel Type

## Slide 12: Risk Factors
Factor # 1 is the base number used to calculate boiler plant rating
Factors # 2 to # 5 add additional percentages to the base Factor #1
Factors # 2 to # 4 may have a significant impact towards the overall plant rating.

## Slide 13: Boiler Plant Classification Attendance Guarded boilers/plants are in yellow
Steam
1st Class - > 30000 kW
2nd Class - 12001 kW to 30000 kW
3rd Class - 8001 kW to 12000 kW
3rd Class - 7001 kW to 8000 kW
4th Class - 4001 kW to 7000 kW
4th Class (8 hrs/day) - 2001 kW to 4000 kW
4th Class (1 insp./24hrs) - 601 kW to 2000 kW
Unattended – 301 kW to 600 kW
Exempt - < 300 kW
Hot Water
2nd Class - > 30000 kW
3rd Class - 12001 kW to 30000 kW
4th Class - 8001 kW to12000 kW
4th Class - 7001 kW to 8000 kW
4th Class (8 hrs/day) - 4001 kW to 7000 kW
4th Class (1 insp./24hrs) - 2001 kW to 4000 kW
Unattended – 601 kW to 2000 kW
Exempt - < 600 kW
Note: In the event that both Steam and Hot Water Boilers are in the same plant, the rating of both shall be combined and classified as the total rating under steam

## Slide 14: 4th Class (8 hrs/day) - 2001 kW to 4000 kW
A boiler shall be attended by a 4th Class Chief Engineer 8 hrs/day between 6:00 and 18:00 Monday to Friday.
Boiler shall be attended by a 4th Class Shift Engineer during any 8 hrs period each 24 hours during Saturday, Sunday, and holidays period the boiler is operating.

## Slide 15: 4th Class (1 insp./24hrs) - 601 kW to 2000 kW
The boiler plant shall be inspected once each 24 hrs day of operation by a Power Engineer to ensure the plant is operating safely in accordance to the manufacturer's recommendation, and such inspections shall be logged. Any safety concerns will be addressed.

## Slide 16: Unattended – 301 kW to 600 kW
The owner/user is responsible to maintain and operate the boiler(s) in accordance with the manufactures recommendations, and shall have a maintenance program that is designed to ensure safe operation and maintenance of boiler(s).

## Slide 17: Determining Boiler Kilowatt Rating
Boiler rating is expressed in kilowatt’s. The boiler nameplate data as determined by the manufacturer is the source of the information.

## Slide 18: Determining Boiler Kilowatt Rating
Applying lb/hr data X .284 = boiler kilowatt rating
Applying kg/hr data X .625 = boiler kilowatt rating
Applying ft² heating surface data X 1 = boiler kilowatt rating
Applying m2 heating surface data X 10 = boiler kilowatt rating
Applying Btu/hr X 0.000293 = boiler kilowatt rating
Note: kW = Boiler horsepower (bhp) X 10

## Slide 19: Risk Factor # 1 Total Installed Capacity
The total plant kilowatt rating for risk factor #1 is determined by adding the individual rating of all boilers.

## Slide 20: Examples Risk Factor # 1 Total Installed kW Capacity
Example 1
Single Boiler Room
Steam Boiler No. 1 = 500 kW
Steam Boiler No. 2 = 750 kW
Total Base kW rating = 1250 kW
Example 2
Two boiler Rooms
Steam Boiler No. 1 = 500 kW
Steam Boiler No. 2 = 500 kW
Steam Boiler No. 3 = 10,000 kW
Steam Boiler No. 4 = 5000 kW
Total Base kW rating = 16,000 kW
Example 3
Three Boiler Rooms
Steam Boiler No. 1 = 1000 kW
Steam Boiler No. 2 = 1000 kW
Steam Boiler No. 3 = 1000 kW
Steam Boiler No. 4 = 500 kW
Steam Boiler No. 5 = 500 kW
Steam Boiler No. 6 = 1500 kW
Total Base kW rating = 5500 kW

## Slide 21: Risk Factor # 2 Number of Boilers
An additional risk factor in percentage is added to the plant installed kW rating for each additional boiler.
  This is to encourage a reduced number of boiler rooms
Number of Boilers | Percentage %
1 | 0%
2 | 10%
3 | 20%
4 | 30%
5 + | 40%

## Slide 22: Example Risk Factor # 2
For each additional boiler over (1), a risk factor penalty of 10 percent is added to the total installed boiler kilowatt rating (base kW rating) to a maximum of 40 percent.
  Example 1 - 2 boilers = 10%
  Example 2 - 4 boilers = 30%
  Example 3 - 6 boilers = 40%

## Slide 23: Risk Factor # 3 Number of Boiler Rooms
An additional risk factor in percentage is added to the plant installed kW rating for each additional boiler room on site.
  This is to encourage a reduced number of boiler rooms
Number of Boiler Rooms | Percentage %
1 | 0%
2 | 20%
3 | 30%
4 | 60%
5 | 90%

## Slide 24: Risk Factor # 4 Boiler Types
An additional risk factor in percentage is added to the installed plant kW total for the various boiler types being used in a plant.
Unfired/electric | = | 0%
Watertube (all types) | = | 2%
HRT/Vertical / addendum ”B” style | = | 4%
Scotch Marine Dry Back/ Sectional | = | 5%
Scotch Marine Wet Back/Firebox/Locomotive | = | 6%
Note: If more than one type of boiler is installed then the highest rated boiler type will apply

## Slide 25: Example Risk Factor # 4 Boiler Types
Example (2) |  | 
Boiler #1 | = | Scotch Marine Dryback
Boiler #2 | = | Scotch Marine Wetback
Wetback Boiler #3 | = | Watertube
Boiler #4 | = | Electric
Additional Risk | = | 6%
Example (1) |  | 
Boiler #1 | = | Scotch Marine Dryback
Boiler #2 | = | Vertical Firetube
Additional Risk | = | 5%
Example (3) |  | 
Boiler #1 | = | Watertube
Boiler #2 | = | Watertube
Boiler #3 | = | Watertube
Boiler #4 | = | HRT Firetube
Boiler #5 | = | Sectional
Boiler #6 | = | Watertube
Additional Risk | = | 5%

## Slide 26: Risk Factor # 5 Fuel Types
An additional risk factor in percentage is added to the installed plant kW total for the fuel types used.
Unfired/electric | = | 0%
Liquid | = | 5%
Gas | = | 10%
Solid Fuel | = | 10%
Pulverized | = | 20%
Black/Red Liquor | = | Automatic 1st Class Plant
When multiple fuels are used the combustion percentage
is the highest of all the fuel types plus 5%.

## Slide 27: Example Risk Factor # 5 Fuel Types
15% to be added to the kW base rating.
15% to be added to the kW base rating.
25% to be added to the kW base rating.
Example (1) |  | 
Gas | = | 10%
Liquid | = | 5%
10% + 5% | = | 15%
Example (2) |  | 
Solid | = | 10%
Liquid | = | 5%
Gas | = | 10%
10% + 5% | = | 15%
Example (3) |  | 
Pulverized | = | 20%
Liquid | = | 5%
Gas | = | 10%
20% + 5% | = | 25%

## Slide 28: Total Plant Kilowatt Rating
This plant is rated as a guarded 4th Class/1 inspection per 24 hour operation
Real Case - Example 1
Boiler 1 – 500 kW - Liquid fired - Scotch marine dry back
Boiler 2 – 750 kW – Gas fired – Vertical
Located in one boiler room:
  1. Total installed kilowatts 500 + 750 = 1250 kW
  2. Two boilers = 10%
  3. One boiler room = 0%
  4. Boiler types = highest of the boiler types = 5%
  5. Multiple fuels = 10% is the highest of the two fuels, so add 5 % = 15%
  6. Total risk factor = 10 + 0 + 5 + 15 = 30%
  7. Additional plant kilowatt risk rating = 1250 x .3 = 375 kW
  8. Final plant rating 1250 + 375 = 1625 kW

## Slide 29
This plant is rated as a 2nd Class plant
Real Case - Example 2
Boiler 1 – 500 kW - Liquid fired - Scotch marine dry back
Boiler 2 – 500 kW – Liquid fired – Scotch marine wet back
Boiler 3 - 10000 kW – Solid fired – Watertube
Boiler 4 - 5000 kW – Electric fired
Located in two boiler rooms:
  1. Total installed kilowatts 500 + 500 + 10000 + 5000 = 16000 kW
  2. Four boilers = 30%
  3. Two boiler rooms = 20%
  4. Boiler types = highest of the boiler types = 6%
  5. Multiple fuels = 10 % is the highest of the three fuels, so add 5 % = 15%
  6. Total additional risk factor = 30 + 20 + 6 + 15 = 71%
  7. Additional plant kilowatt risk rating = 16000 x .71 = 11360 kW
  8. Final plant rating 16000 + 11360 = 27360 kW

## Slide 30
Real Case - Example 3
Boiler 1 - 1000 kW - Gas fired – Watertube
Boiler 2 - 1000 kW - Gas fired – Watertube
Boiler 3 - 1000 kW - Gas fired – Watertube
Boiler 4 - 500 kW - Liquid fired – HRT
Boiler 5 - 500 kW - Liquid fired – Sectional
Boiler 6 - 1500 kW – Solid Fuel – Watertube
Located in three boiler rooms:
  1. Total installed kilowatts =1000 + 1000 + 1000 + 500 + 500 + 1500 = 5500 kW
  2. Six boilers = 40%
  3. Three boiler rooms = 30%
  4. Multiple fuels = 10% is the highest of the three fuels, so add 5 % = 15%
  5. Boiler types = highest of the boiler types = 5%
  6. Total risk factor = 40 + 30 + 15 + 5 = 90%
  7. Additional plant kilowatt risk rating = 5500 x .9 = 4950 kW
  8. Final plant rating 5500 + 4950 = 10450 kW
This is rated as a 3rd Class plant

## Slide 31: Definitions
Boiler – means a vessel in which steam or other vapour can be generated or in which a liquid can be heated, by the application of a heat source at a pressure above atmospheric.(still on going discussions)
Steam Plant – means an installation consisting of boiler(s), auxiliary equipment and related piping systems, in which steam can be generated by the application of a heat source at a pressure above atmospheric.
High Temperature Hot Water Plant – means an installation consisting of boiler(s), auxiliary equipment and related piping systems, in which water can be heated by the application of a heat source at a temperature at or above 100 C (212 F).

## Slide 32: Definitions
Boiler horsepower (bhp) – means 15.6 kg (34.5 lb) of water evaporated from and at 100 C (212 F) (33475 BTU/hr.,9.8 kW)
Firetube boiler – means a boiler that consists of fire tubes within which pass the products of combustion and or hot gases and that are cooled externally by the boiler.
High Temperature Hot Water – means water at or above 100 C (212 F).
Watertube boiler – means any type of boiler that consists of water tubes within which passes the boiler water where the water tubes are heated externally by a combustion process.
Sectional Boiler – means a boiler constructed of cast metal sections.
Electric Boiler – means a boiler using electric energy in immersion, resistor, or electrode elements, as the source of heat

## Slide 33: Outstanding Issues (not part of the presentation) Under Review
The qualification time/level of experience for the various levels for Power Engineers should be standardized all across Canada
Requirements for accepting Power Engineering College Programs need to be developed for mutual acceptance among jurisdictions.
Designing a standardized set of plant classification rules for Refrigeration, Compressor, and Steam Prime Mover plants
Encourage the incorporation of the Quebec Operating Engineer system into the SOPEEC system at all levels